## BOQ
KRATU Estimate
AI BOQ/BOM Estimation Engine — NBC 2016 Compliant
19 July 2026
COMMERCIAL PROPOSAL — Test GroundFloor — Fire Protection BOQ
Scope: Whole Building
Description | Specification | Qty | Unit | Unit Rate (₹) | Amount (₹)
SPRINKLER SYSTEM
Sprinkler Head (Concealed Pendent) - 68°C | SPR-001 — Source: cad_exact | 24 | Nos | 850 | 20400
Sprinkler Armover with Escutcheon Plate | SPR-002 | 24 | Nos | 350 | 8400
CPVC Pipe 25mm (1") - Branch Line | SPR-003 — Approx 2.5m per head avg | 20 | RMT | 180 | 3600
CPVC Pipe 40mm (1.5") - Cross Main | SPR-004 — Based on floor area | 73 | RMT | 280 | 20440
CPVC Pipe 65mm (2.5") - Range Pipe | SPR-005 | 9 | RMT | 450 | 4050
Alarm Check Valve with Trim | SPR-010 | 1 | Nos | 18500 | 18500
OS&Y Gate Valve (ICV) | SPR-011 | 1 | Nos | 8500 | 8500
Flow Switch | SPR-012 | 1 | Nos | 4500 | 4500
Pressure Gauge | SPR-013 | 4 | Nos | 800 | 3200
Drain Valve 25mm | SPR-014 | 3 | Nos | 1200 | 3600
Test and Drain Valve Assembly | SPR-015 | 1 | Nos | 6500 | 6500
Main Drain Valve Assembly | SPR-016 | 1 | Set | 8500 | 8500
YARD HYDRANT
Underground CI Pipe 150mm | YH-001 | 90 | RMT | 1100 | 99000
Double Outlet Yard Hydrant with Landing Valve | YH-002 — Source: cad_exact | 3 | Nos | 8500 | 25500
Yard Hydrant Chamber with Cover | YH-003 | 3 | Nos | 3800 | 11400
Gate Valve 150mm | YH-004 | 4 | Nos | 5500 | 22000
FIRE PUMP SET
Electric Fire Pump 2270 LPM @ 33m | FP-001 | 1 | Nos | 285000 | 285000
Diesel Fire Pump 2270 LPM @ 33m | FP-002 | 1 | Nos | 350000 | 350000
Jockey Pump 50 LPM @ 43m | FP-003 | 1 | Nos | 48000 | 48000
Pump Suction Header with Valves | FP-004 | 1 | Set | 25000 | 25000
Pump Delivery Header with Valves | FP-005 | 1 | Set | 25000 | 25000
Diesel Fuel Tank 500L with Level Gauge | FP-006 | 1 | Nos | 25000 | 25000
Pump Room Piping and Fittings | FP-007 | 1 | LS | 45000 | 45000
Cumulative Flow Meter | FP-008 | 1 | Nos | 8500 | 8500
Pressure Switches and Gauges | FP-009 | 1 | Set | 12000 | 12000
HOSE REEL SYSTEM
Hose Reel with 20m Rubber Hose | HR-001 — Source: cad_exact | 6 | Nos | 5500 | 33000
GI Pipe 25mm for Hose Reel | HR-002 | 30 | RMT | 95 | 2850
Isolating Valve 25mm | HR-003 | 6 | Nos | 850 | 5100
FIRE EXTINGUISHER
ABC Type Fire Extinguisher 4.5kg | FE-001 — Source: cad_exact | 9 | Nos | 3200 | 28800
CO2 Fire Extinguisher 4.5kg | FE-002 | 4 | Nos | 4500 | 18000
Extinguisher Bracket/Stand | FE-003 | 8 | Nos | 450 | 3600
DETECTION & ALARM
Main Fire Alarm Control Panel | FA-001 | 1 | Nos | 95000 | 95000
Repeat Indicator Panel (Ground Floor) | FA-002 | 1 | Nos | 18000 | 18000
Manual Call Point (Break Glass) | FA-003 | 6 | Nos | 2200 | 13200
Photoelectric Smoke Detector | FA-004 | 13 | Nos | 1800 | 23400
Heat Detector (Fixed Temp 68°C) | FA-005 | 2 | Nos | 1600 | 3200
Electronic Hooter 110dB | FA-006 | 4 | Nos | 2500 | 10000
Fire Alarm Cable (2-core) | FA-007 | 315 | RMT | 25 | 7875
MCB and Distribution Board for FA System | FA-008 | 1 | Set | 8500 | 8500
WATER STORAGE
Fire Water Storage Tank - 175 KL RCC Underground | WT-001 — Sprinkler 111 KL + Hydrant 50 KL | 175 | KL | 5000 | 875000
Tank Internal Waterproofing (2-coat) | WT-002 | 1 | Nos | 85000 | 85000
Float Type Level Indicator with Alarm | WT-003 | 1 | Nos | 12000 | 12000
Tank Access Ladder with Safety Cage | WT-004 | 1 | Nos | 18000 | 18000
Tank Overflow and Drain Arrangement | WT-005 | 1 | Set | 15000 | 15000
Suction Pipe from Tank to Pump Room | WT-006 | 1 | Set | 35000 | 35000
Tank Make-up Water Connection with Float Valve | WT-007 | 1 | Nos | 8500 | 8500
CIVIL WORKS
Trench Excavation for Underground Piping (600mm deep) | CW-001 | 90 | RMT | 850 | 76500
Trench Backfilling and Compaction | CW-002 | 90 | RMT | 450 | 40500
Concrete Thrust Blocks at Bends and Junctions | CW-003 | 6 | Nos | 5000 | 30000
Pump Foundation and Base Frame (Grouting) | CW-004 | 3 | Nos | 15000 | 45000
Pump Room Floor Drain and Sump Pit | CW-005 | 1 | Nos | 25000 | 25000
Pump Room Ventilation Louvers | CW-006 | 1 | Nos | 12000 | 12000
PIPE SUPPORTS
Pipe Hanger (Clevis Type) for Sprinkler System | PS-001 | 34 | Nos | 350 | 11900
Seismic Brace for Sprinkler Piping | PS-002 | 9 | Nos | 800 | 7200
Pipe Clip and Bracket for Hose Reel Piping | PS-004 | 24 | Nos | 150 | 3600
Miscellaneous Fittings (Elbows, Tees, Reducers) | PS-005 | 1 | LS | 25000 | 25000
PAINTING & ID
NBC Color Code Identification Bands and Labels | PT-002 | 1 | LS | 35000 | 35000
Fire Safety Signage (Illuminated - Photoluminescent) | PT-003 | 9 | Nos | 2500 | 22500
Valve Identification Tags (Brass) | PT-004 | 8 | Nos | 350 | 2800
Pipe Flow Direction Arrows and System Labels | PT-005 | 3 | Nos | 150 | 450
TESTING & COMMISSIONING
Hydrostatic Pressure Test (All Piping Systems) | TC-001 | 1 | LS | 50000 | 50000
Sprinkler System Flow Test and Coverage Verification | TC-002 | 1 | Nos | 25000 | 25000
Fire Pump Performance and Characteristic Test | TC-003 | 3 | Nos | 15000 | 45000
Fire Alarm System Commissioning and Sound Test | TC-004 | 1 | LS | 35000 | 35000
Final Acceptance Test, Documentation and Handover | TC-005 | 1 | LS | 50000 | 50000
CONTINGENCY
Unforeseen Items and Site Contingencies (5% of estimated base) | CG-001 — 5% of base cost = Rs.1,48,000 | 1 | LS | 148000 | 148000
|  |  | Basic Material Cost |  | 3101065
|  |  | Agency Overheads |  | 310106.5
|  |  | Agency Profit |  | 511675.73
|  |  | GST |  | 706112.5
|  |  | GRAND TOTAL |  | 4628959.73
Amber unit-rates are estimated from NBC 2016 references — verify against your rate card before quoting.
Engineered by KRATU AI Labs · NBC 2016 Compliant