## BOQ
KRATU Estimate
AI BOQ/BOM Estimation Engine — NFPA Compliant
August 31, 2026
COMMERCIAL PROPOSAL — us test office — Fire Protection Estimate
Scope: Whole Building
Description | Specification | Qty | Unit | Unit Rate ($) | Amount ($)
SPRINKLER SYSTEM
Automatic Sprinkler Head (Pendent/Upright, 155°F) - QR | USPR-001 — Source: nfpa_estimated; ordinary_2 hazard @ 0.2 gpm/ft² | 509 | EA | 18 | 9162
Sprinkler Escutcheon / Cover Plate | USPR-002 | 509 | EA | 4 | 2036
Branch Line Pipe 1" (CPVC/Sch10 steel) | USPR-003 — Approx 8 LF per head | 4072 | LF | 9 | 36648
Cross Main Pipe 2" (Sch10 steel) | USPR-004 — Based on floor area | 600 | LF | 14 | 8400
Feed Main / Riser Pipe 4" (Sch40 steel) | USPR-005 | 72 | LF | 32 | 2304
Riser Assembly w/ Alarm Check Valve | USPR-010 | 2 | EA | 2800 | 5600
Control Valve (OS&Y) w/ Tamper Switch | USPR-011 | 2 | EA | 850 | 1700
Waterflow Switch | USPR-012 | 2 | EA | 320 | 640
Pressure Gauge | USPR-013 | 4 | EA | 45 | 180
Inspector's Test & Drain Valve Assembly | USPR-014 | 2 | EA | 450 | 900
Auxiliary Drain (per floor) | USPR-015 | 6 | EA | 180 | 1080
STANDPIPE SYSTEM
Standpipe Riser 6" (Sch40 steel) | USTP-001 | 196 | LF | 85 | 16660
2.5" Class I Hose Valve w/ Pressure-Reducing (per floor) | USTP-002 — Source: nfpa_calculated | 14 | EA | 650 | 9100
Hose Valve Cabinet | USTP-003 | 14 | EA | 380 | 5320
Check Valve 6" | USTP-004 | 2 | EA | 1200 | 2400
Control/Isolation Valve 6" w/ Tamper | USTP-005 | 2 | EA | 1400 | 2800
Air/Vacuum Relief Valve | USTP-006 | 2 | EA | 280 | 560
Pressure Gauge (per riser) | USTP-007 | 4 | EA | 45 | 180
Riser Connection to Pump Header | USTP-008 | 2 | Set | 1500 | 3000
FIRE DEPT CONNECTION
Fire Department Connection (Siamese, 4"x2.5"x2.5", Storz) | USFDC-001 | 2 | EA | 1800 | 3600
FDC Check Valve & Connection to System | USFDC-002 | 1 | Set | 900 | 900
FDC Identification Signage | USFDC-003 | 1 | EA | 60 | 60
FIRE HYDRANTS
Underground Fire Main 6" (C900 PVC/DI) | USYH-001 — Approx 100 LF per hydrant | 200 | LF | 95 | 19000
Dry-Barrel Fire Hydrant (AWWA) | USYH-002 — Source: nfpa_calculated | 2 | EA | 4500 | 9000
Post Indicator Valve (PIV) | USYH-003 | 1 | EA | 2800 | 2800
Gate Valve 6" w/ Valve Box | USYH-004 | 3 | EA | 1400 | 4200
FIRE PUMP
Electric Fire Pump 1000 GPM @ 153 psi (UL/FM) | USFP-001H | 1 | EA | 65000 | 65000
Diesel Fire Pump 1000 GPM @ 153 psi (UL/FM) | USFP-002H | 1 | EA | 95000 | 95000
Jockey (Pressure Maintenance) Pump | USFP-003 | 1 | EA | 4200 | 4200
Suction Header w/ Valves & Fittings | USFP-004 | 1 | Set | 6500 | 6500
Discharge Header w/ Valves & Fittings | USFP-005 | 1 | Set | 6500 | 6500
Fire Pump Controller (Listed) | USFP-006 | 2 | EA | 9500 | 19000
Diesel Fuel Tank w/ Level Gauge | USFP-007 | 1 | EA | 7500 | 7500
Flow Meter & Test Header | USFP-008 | 1 | Set | 5500 | 5500
Pressure Relief Valve & Sensing Lines | USFP-009 | 1 | Set | 3800 | 3800
HOSE STATIONS
1.5" Hose Station w/ Rack & Nozzle | USHS-001 — Source: nfpa_calculated | 6 | EA | 650 | 3900
1.5" Pipe & Valve to Hose Station | USHS-002 | 90 | LF | 12 | 1080
Isolation Valve 1.5" | USHS-003 | 6 | EA | 180 | 1080
FIRE EXTINGUISHER
ABC Dry Chemical Extinguisher 10 lb | USFE-001 — Source: nfpa_calculated; max travel 75 ft | 30 | EA | 85 | 2550
CO2 Extinguisher 10 lb (electrical) | USFE-002 | 13 | EA | 220 | 2860
Extinguisher Cabinet / Bracket | USFE-003 | 42 | EA | 180 | 7560
DETECTION & ALARM
Fire Alarm Control Panel (FACP, addressable) | USFA-001 | 1 | EA | 6500 | 6500
Remote Annunciator (at main entrance) | USFA-002 | 1 | EA | 1400 | 1400
Manual Pull Station (dual-action) | USFA-003 | 14 | EA | 75 | 1050
Photoelectric Smoke Detector (addressable) | USFA-004 | 17 | EA | 65 | 1105
Heat Detector (135°F fixed/ROR) | USFA-005 | 3 | EA | 55 | 165
Horn/Strobe Notification Appliance (ADA) | USFA-006 | 20 | EA | 85 | 1700
FPLR Fire Alarm Cable | USFA-007 | 2700 | LF | 2.5 | 6750
Batteries / Power Supply / NAC Booster | USFA-008 | 1 | Set | 1200 | 1200
Duct Smoke Detector (HVAC shutdown) | USFA-009 | 3 | EA | 320 | 960
WATER SUPPLY
Fire Water Storage Tank 60,000 gal | USWT-001 — 1000 gpm x 60 min (ordinary_2) | 60000 | gal | 2.5 | 150000
Tank Interior Coating / Lining | USWT-002 | 1 | EA | 8500 | 8500
Level Indicator w/ Low-Level Alarm | USWT-003 | 1 | EA | 1200 | 1200
Tank Access Ladder w/ Safety Cage | USWT-004 | 1 | EA | 1800 | 1800
Overflow & Drain Arrangement | USWT-005 | 1 | Set | 1500 | 1500
Suction Pipe to Pump Room | USWT-006 | 1 | Set | 3500 | 3500
Automatic Fill Valve (make-up water) | USWT-007 | 1 | EA | 850 | 850
CIVIL WORKS
Trench Excavation for Underground Main (36" cover) | USCW-001 | 200 | LF | 28 | 5600
Backfill & Compaction | USCW-002 | 200 | LF | 12 | 2400
Concrete Thrust Blocks at Bends/Tees | USCW-003 | 4 | EA | 450 | 1800
Fire Pump Housekeeping Pad / Foundation | USCW-004 | 3 | EA | 1500 | 4500
Pump Room Floor Drain & Sump | USCW-005 | 1 | EA | 2500 | 2500
Pump Room Ventilation Louvers | USCW-006 | 1 | EA | 1200 | 1200
PIPE SUPPORTS
Pipe Hanger (listed) for Sprinkler Piping | USPS-001 | 475 | EA | 18 | 8550
Seismic Sway Brace (lateral/longitudinal) | USPS-002 | 119 | EA | 95 | 11305
Riser Clamp / Support for Standpipe | USPS-003 | 24 | EA | 45 | 1080
Misc. Fittings (elbows, tees, reducers) | USPS-005 | 1 | LS | 3500 | 3500
PAINTING & ID
Pipe Identification Labels & Flow Arrows | USPT-002 | 1 | LS | 2500 | 2500
Fire Safety Signage (photoluminescent) | USPT-003 | 21 | EA | 45 | 945
Valve Identification Tags | USPT-004 | 8 | EA | 18 | 144
TESTING & COMMISSIONING
Hydrostatic Test (200 psi / 2 hr, all piping) | USTC-001 | 1 | LS | 4500 | 4500
Sprinkler Flow Test & Final Inspection | USTC-002 | 1 | EA | 2500 | 2500
Fire Pump Acceptance Test (churn/rated/150%) | USTC-003 | 3 | EA | 3500 | 10500
Fire Alarm Acceptance Test & Programming | USTC-004 | 1 | LS | 3500 | 3500
Final Acceptance, O&M Manuals, As-Builts, Handover | USTC-005 | 1 | LS | 5000 | 5000
SMOKE CONTROL
Stair Pressurization Fan w/ Motor | USSC-001 — 1 per exit stair | 2 | EA | 12000 | 24000
Galvanized Ductwork for Pressurization | USSC-002 | 44 | LF | 65 | 2860
Motorized Smoke/Fire Damper | USSC-003 | 4 | EA | 850 | 3400
Differential Pressure Sensor (per floor) | USSC-004 | 6 | EA | 450 | 2700
Smoke Control Panel (Firefighter Smoke Control Station) | USSC-005 | 1 | EA | 18000 | 18000
Fresh Air Intake Louver w/ Filter | USSC-006 | 2 | EA | 1800 | 3600
Smoke Exhaust Fan w/ Motor | USSC-010 — Basement smoke removal | 2 | EA | 9500 | 19000
Makeup Air Fan w/ Motor | USSC-011 | 2 | EA | 7500 | 15000
Smoke Exhaust Ductwork (galvanized) | USSC-012 | 100 | LF | 75 | 7500
Fire-Rated Motorized Smoke Damper | USSC-013 | 4 | EA | 950 | 3800
EMERGENCY LIGHTING
LED Exit Sign (90-min battery) | USEL-001 | 28 | EA | 85 | 2380
Emergency Egress Light (LED, 90-min) | USEL-002 | 42 | EA | 120 | 5040
Central Inverter / Battery Unit | USEL-003 | 1 | EA | 8500 | 8500
Fire-Rated (2-hr) Circuit Wiring | USEL-004 | 210 | LF | 6 | 1260
VOICE EVACUATION
Voice Evacuation Amplifier / Controller | USVE-001 | 1 | EA | 6500 | 6500
Ceiling Speaker / Speaker-Strobe | USVE-002 | 42 | EA | 95 | 3990
Firefighter Telephone / Communication | USVE-003 | 7 | EA | 320 | 2240
Fire-Rated Speaker Circuit Cable | USVE-004 | 420 | LF | 3 | 1260
FIRE SERVICE ELEVATOR
Firefighter Emergency Operation (Phase I/II recall) | USFL-001 | 1 | EA | 8500 | 8500
Elevator Lobby Smoke Detector (recall) | USFL-002 | 6 | EA | 85 | 510
Shunt Trip / Elevator Power Monitoring | USFL-003 | 1 | Set | 2500 | 2500
Elevator Machine Room Heat Detector | USFL-004 | 1 | EA | 65 | 65
FIRE ELECTRICAL
Fire Pump Disconnect / Monitoring | USEE-001 | 1 | EA | 2500 | 2500
Fire-Rated Power Feed to Pump/FACP | USEE-002 | 151 | LF | 18 | 2718
CONTINGENCY
Contingency & Unforeseen Site Conditions (5% of base) | USCG-001 — 5% of base = $39,500 | 1 | LS | 39500 | 39500
|  |  | Basic Material Cost |  | 827787
|  |  | Agency Overheads |  | 82778.7
|  |  | Agency Profit |  | 91056.57
|  |  | Sales Tax |  | 82633.84
|  |  | GRAND TOTAL |  | 1084256.11
Amber unit-rates are estimated from NFPA references — verify against your rate card before quoting.
Preliminary budgetary estimate for bidding/planning. Quantities and sizing are based on published NFPA baseline criteria and must be verified by a licensed PE / NICET-certified designer with a project-specific hydraulic calculation before construction or permit submission.
Engineered by KRATU AI Labs · NFPA Compliant